TECHNO-COMMERCIAL OFFER

FOR

SIB STEAM BOILER MINIMAC 0.6 /AGWF

Quotation No: 3012/1231/21-22

Date: 30.12.2021

Submitted To

M/S. MEGAFARM AGRO PRODUCER COMPANY L. Site: WAI-SATARA.

Submitted By

RELIABLE THERMAL ENGINEERS D-13, MIDC, MAHAD

RAIGAD, MAHARASHTRA - 401309 INDIA

| GM | ABHILASH GEORGE |
| --- | --- |
| Office | Mahad |
| Phone No | +91-8888842253 |
| Email Id | sales@reliablethermal.com |
| Website | www.reliablethermal.com |

Ref. No. RTE/MAPCL/3012/1231/21-22

December 30, 2021

To,

M/s. Megafarm Agro Producer Company Ltd.

Plot No B-193, MIDC- Wai.

Kind Attn: Mr. Nilesh

Subject:Quotation For 0.6 TPH SIB STEAM BOILER.

Dear Sir,

We thank you for the telephonic discussion you had with us, and as discussed, we are very much pleased to submit our offer for the following.

System: SIB STEAM BOILER

Model: MINIPAC 06

Fuel: COAL/BRIQUTTE/WOOD.

We take this opportunity to highlight the range of products offered by RELIABLE THERMAL ENGINEERS:

| Thermic Fluid Heater : | Upto 80 Lac Kcal/Hr | :Liquid, Gas, Solid Fuel Fired |
| --- | --- | --- |
| Non-IBR Steam Boiler : | Upto 850 Kg/Hr | :Liquid, Gas Fired |
| IBR Steam Boiler : | Upto 50 TPH | :Liquid, Gas, Solid Fuel Fired |

Kindly go through our proposal to favor us with your valued order. Thanking you and assuring you of our best service at all time.

Yours Faithfully,

For RELIABLE THERMAL ENGINEERS

Kajal

INDEX

Annexure I	Customer Data

Annexure II	Technical Specifications

Annexure III	Scope of Supply

Annexure IV	Make of Bought outs

Annexure V	Battery Limits

Annexure VIII	Exclusion List

Annexure IX	Price Schedule

Annexure X	Commercial Terms & Condition

Annexure XI	General Terms & Condition for Sale

Annexure I

CUSTOMER DATA (TO BE CONFIRMED)

Site Data

Location:	Raigad.

Altitude:	< 500 mtr above mean sea level. Ambient Temperature: Maximum 35 Deg C

Minimum 22 Deg C

Humidity:	40 % Average

Wind Speed:	As per IS 875

Seismic Coefficient:	As per IS 1893

Fuel Data

Type:	Indonesian Coal /Wood/Briquettes/

GCV of Fuel:	5500/ 3200/3760 kcal/Kg

Ash:	5-6%/5-12% Maximum

Total Moisture:	5%/7%/25% Maximum

Size:	150 mm to 300 mm for Wood 40 mm to 50 mm for Briquettes 20 mm to 25 mm for coal

Electrical Data

Voltage:	415 V + 10%

Frequency:	50 Hz + 3%

Combined:	+ 10%

With Solid Earth

3 Phase, 4 Wire System

Compressed Air

Quality:	Instrument Air

Pressure:	7 Bar with FRL

Water

Specification:	As mention in our techno Commercial offer

Annexure II

TECHNICAL SPECIFICATIONS

| Sr. No | OPERATING PARAMETERS | UNIT | MINIPAC 06 |
| --- | --- | --- | --- |
| 1. | Steam Generation Capacity (F & A 100˚ C) | Kg / Hr | 600 |
| 2. | Safety valve lift of pressure (SVLOP) | Kg / cm² | 7 |
| 3. | Hydraulic Test Pressure | Kg / cm² | 10.5 |
| 4. | Efficiency of Boiler on GCV basis – GCV of Wood : 3200 kcal/kg GCV of Briquettes : 3760 kcal/kg GCV of Indonesian Coal : 5500 Kcal/kg | % | 72± 2 % Based on GCV of Wood 74± 2 % Based on GCV of Briquettes 76± 2 % Based on GCV of Coal |
| 5. | Fuel Consumption (Approx.) (At Full Load) | Kg/hr | 118 kg/hr of Wood at full load 98 kg/hr of Briquettes at full load 65 kg/hr of Coal at full load |
| 6. | Steam Quality (Dryness) | % | 98% Dry Saturated |
| 7. | Fuel Feeding System |  | Manual |
| 8. | Flue Gas Temperature Boiler WPH STACK/CHIMNEY | Deg C | 220 180 160 |
| 9. | Grate Type |  | Stationary Grate Bars with Supports |
| 10. | Boiler Design/ Construction |  | IBR 1950 with Latest Amendments. |
| 11. | Type of Boiler |  | Smoke Tube Package Type |
| 12. | Number of Furnace |  | 1 No. |
| 13. | Steam / Water Separator |  | Inbuilt |
| 14. | Boiler House Dimensions | mm | 5000 L * 4000 W * 4500 H |

Annexure III

SCOPE OF BOILER

- Shell and Tube Assembly

Boiler shell is constructed in suitable sections dependent upon boiler size. Following the rolling process, longitudinal and circumferential seams are machine welded and subjected to X-Ray and NDT inspection to comply with the latest standard requirements with required Manholes; Hand-holes etc. mounted on Saddles;

Access doors permit as far as is practicable, the internal inspection of heating surfaces and include a main door on top of the boiler shell and one mud door is provided in the rear tube plate.

Construction Material

| Shell, Furnace and Tube Plates | SA 516 GR 70 / Equivalent |
| --- | --- |
| Furnace Access Tube | SA 516 GR 70 / Equivalent |
| Plain and Stay Tubes | BS 3059 ERW 320 & BS 3059 GR 360 |
| Man door Mud door Lifting Lug | A – 531 C l – 1 |
| Pads | SA 516 GR 70 / Equivalent |
| Bosses | SA 516 GR 70 / Equivalent |
| Stand pipes | SA 106 Gr B |

- Insulation and Cladding

The external surface of the boiler shell and the periphery of the front Smoke Box are to be insulated with min 75 mm thick mineral wool/Rockwool slabs securely fixed and clad in min GI cladding 0.7 mm Thk.

- Mountings and Fittings

Mountings and controls are fitted to pads and nozzles welded to boiler shell. Below are the makes of mountings and fittings on the boiler. They shall be supplied with boiler as per IBR formalities and as per the requirement of Day-to-Day Operation & Maintenance.

| Sr. No. | Description | Qty. |
| --- | --- | --- |
| 1 | Safety Valves | 2 No’s |
| 2 | Main Steam Stop Valve | 1 No. |
| 3 | Isolation & Drain Valves | 4No’s |
| 3 | Blow Down Valve | 1 No. |

| 4 | Water Level Gauge | 2 No’s |
| --- | --- | --- |
| 5 | Pressure Gauge | 1 No. |
| 6 | Pressure switch | 1 No. |
| 7 | Fusible Plug | 1 No. |
| 8 | Feed Check Valves | 1 No. |
| 9 | Water Level Controller | 1 No. |
| 10 | Feed Water Inlet Valve | 1 No. |

- BOILER FEED WATER PUMPS

| Type |  | Multistage pump |
| --- | --- | --- |
| Capacity | M3/hr. | 1 |
| Total differential head | MLC | 80 |
| No. of pumps in operation |  | One |
| Speed | RPM | 2900 |
| Max. Operating temperature | OC | 90 |
| Motor rating | HP | 1.5 |

- Draught Fans (ID fan)

Type	: Centrifugal

Capacity	: 1100 m3/hr

Total differential pressure developed	: 200 mmWc Design Temp	: 180°C

Fan speed	: 2900 rpm

Motor rating	: 2 HP

- Control Panel

It will be Self-Standing /skid mounted Cabinet. It will be Powder Coated, prewired & will consist of the following:

-- Power Circuit

-- Control Fuses and Contactors.

-- Control Switches & Push Buttons

-- Indicating Lamps.

-- Hooter

-- Labelling

-- Main Supply – 415V/3 Phase 50Hz

-- Control Supply – 240V/50Hz

Annexure IV

MAKES OF BROUGHT OUTS:

| -- Feed Water Pumps | -- Grundfos/CNP/ Equivalent |
| --- | --- |
| -- Fans | --RTE |
| -- Gauge Glass {Water Level} | -- Mala/Utam Synerchon/ Equivalent |
| -- Valves | -- Mala/Utam Synerchon/ Equivalent |
| -- Safety Valves | -- Brightech / Darling Muesco |
| -- Blow Down Valve | -- Levcon /Equivalent |
| -- Electric Motors | -- CG/ Equivalent |
| -- MCC / Control Panel | -- RTE |
| -- Switchgear Components | -- Siemens/Schneider/ Equivalent |
| -- Steam Pressure Gauge | -- Uttam |
| -- Thermocouples | -- Nutech / Toshniwal/ Equivalent |
| -- Pressure Switches | -- Indfoss / Danfos / Equivalent |

Annexure VII

BATTERY LIMITS

Fuel:	Fire Door

Ash:	Ash discharge points from furnace / Smoke Box

Air:	Suction of Furnace

Electrical:	Incoming & Outgoing Terminals of Control Panel

Incoming Terminals of motors & Field Instruments Earthing Point of Equipment & Panel

Compressed Air:	Incoming point of instrument Water:	Suction of Feed Water Pump

Steam:	Outlet of Main Steam Stop, Safety, and Vent Valve.

Outlet of Blow-down and Drain Valve

Outlet of Drain Valve of Gauge Glass & Mobery

Flue Gas:	Outlet of Boiler

Incoming & Outgoing Flange of ID Fan

WATER QUALITY REQUIREMENT:

Extract from IS 10392 – 1982, Specification for feed water and Boiler water for low and medium land Boilers.

| Characteristics |  | Requirement |
| --- | --- | --- |
| Feed water |  |  |
| Total hardness (as CaCO3) Maximum | PPM | Less than 5 PPM |
| pH value at 25 OC |  | 8.5 to 9.5 |
| Dissolved Oxygen Maximum | PPM | 0.01 |
| Total Iron Maximum | PPM | 0.01 |
| Total Copper Maximum | PPM | 0.01 |
| Silica (as SiO2) Maximum | PPM | 0.05 |
| Conductivity at 25 OC | s/cm | 2.0 |
| Hydrazine Residual | PPM | 0.02 – 0.04 |
| Boiler Water |  |  |
| Total hardness (of filtered Sample) (as CaCO3) | PPM | Not detectable |
| PH Value at 25 OC |  | 10.0 to 10.5 |
| Residual Sodium Sulphate (as Na2SO3) Maximum | PPM | Non – Detectable |
| Residual hydrazine as (N2H4) | PPM | 0.05 to 0.3 |
| Phosphates (as PO4), (if added) | PPM | 25 to 30 |
| Total dissolved solids Maximum | PPM | 1200 |
| Silica (as SiO2). Maximum | PPM | 3.0 |

SAFETY PRECAUTIONS

| Sr. No. | Unsafe Condition | Controller | Controlling Action |
| --- | --- | --- | --- |
| 1. | Extra low-water level in Boiler | Level Controller | Starts the feed water pump to maintain the water level range required. |
| 2. | Very extra low-water level in Boiler | Fusible Plug | Melting of the fusible plug at high temperature, suddenly bringing down the pressure and quenches the fire with water. |
| 3. | Steam Pressure High | Pressure Switch | It trips the ID FAN to control the pressure. |
| 4. | Steam Pressure High | Safety Valve | Opening of safety valve to balance the pressure. |

Annexure VIII

EXCLUSIONS.

  - All Interconnecting Ducting & Chimney.

  - All Water Tank and Water piping

  - Piping – Steam piping, boiler house piping, and condensate piping.

  - PRS & CRS & Steam Distribution Header.

  - Wet Scrubber & Bag Filter.

  - Fuel and Ash handling system beyond our battery limits

  - Water Piping up to Water Softener

  - Condensate Recovery piping

  - Any Steam piping, Blow down Piping beyond our battery limits. (Any Process piping from & After PRS).

  - Electrical cabling incoming terminals of our control panel.

  - Underground Earthling, Earth termination & earth pit.

  - Utilities (water, power, air, gas, etc.) and consumables required for assembling,

  - Erecting and Commissioning of Supplied Material.

  - Fuel, water, instruments and Accessories for commissioning, operation and for performance testing of boiler

  - Clearance from statutory bodies, regulatory authorities like Air Pollution Board, Electricity Board, Factory Inspector, etc.

  - Boiler house or any enclosure for Boiler, lighting & ventilation / air conditioning.

  - Crane for unloading & Erection of Supplied Equipment.

  - All civil design & civil work, cable trenches & blow down / drain pits

  - Any Third Party Inspection

  - Transport, Transit Insurance

  - Any Item not mentioned in our scope of supply

Annexure IX

PRICE SCHEDULE

| SR. NO | DESCRIPTION | QTY | PRICE (INR) |
| --- | --- | --- | --- |
| 1. | Supply of MINIPAC 06 Skid Mounted Biomass Briquettes Wood Fired Boiler 600 kg/hr, SVLOP 7 kg/cm² at F & A 100ºC with, - All IBR mountings, fittings, Valves - ID fan with Motor - Feed Water Pumps - Control Panel - Flue Gas Duct from ID fan to Chimney as per std. layout | 1 Set | Rs.6,90,000/- |
| 2. | Supply of Multi cyclone Dust Collector with Leg Supports. (As a pollution control equipment) | 1 No. | Rs.75,000/- |
| 3. | Softner Assembly 150 ltr with MPV internal line, Resin, & 1 HP Pump | 1 No. | Rs.85,200/- |
| 4. | PRS Station and pipeline ( Boiler to PRS and blow down line) Pressure reduce from 10.54kg to 3.5 kg | 1 No | Rs.3,12,000./- |
| 5. | Water Pre Heater Shell Tube Type( OPTIONAL) | 1 No | Rs.85,000/- |
| 6. | Charges for IBR Formalities & Boiler Registration |  | Rs.70,000.00/- |
|  | TOTAL INR |  | 1317200.00.00 |
|  | SGST 9% |  | 118548.00 |
|  | CGST 9 |  | 118548.00 |
|  | GRAND TOTAL INR |  | 1554296.00 |

Annexure X

COMMERCIAL TERMS & CONDITIONS

| Sr. No | Description |  |
| --- | --- | --- |
| 1. | Price Basis | Ex works Mahad |
| 2. | Packaging & Forwarding | Extra @ 2%. |
| 3. | GST. | Extra as applicable at the time of dispatch. However, prevailing rate is 18 %. |
| 4. | Payment Terms | Supply of Material. 50% Advance along with P.O 50% Inclusive of taxes and duties against pro-forma Invoice to be paid one week prior to dispatch. |
| 5. | Delivery | Boiler will ready for dispatch at our works within6-8week from the date of receipt of Technically & Commercially clear order with requisite Advance. |
| 6. | Terms | As per enclosed Terms & Conditions of Supply. |
| 8. | Transportation & Transit Insurance | Client Scope |
| 9. | Validity | 30 Days |
| 10. | Warranty | 12 months from the date of commissioning or 18 months from the date of dispatch, whichever is earlier |

FOR RELIABLE THERMAL ENGINEERS

Kajal

TERMS & CONDITIONS OF SALE

- Prices:

Unless otherwise stated in writing, all prices are ex-works, Pune / ex-our supplier's work in case part of the goods are manufactured at their works and are exclusive of packing, loading, forwarding, handling freight, transit insurance, etc. All taxes, excise and other duties and levies as applicable at the time of delivery shall be charged separately. Octroi, if any, shall be borne by the buyer. The buyer registered under the sales tax a ct is advised to send sales tax form if any, along with the purchase order. Otherwise, the State/central tax will be charged at full rate as applicable. Prices are subjected to verification depending on raw material cost.

- Delivery:

Delivery RTEs quoted are subject to prior sale and confirmation by us. Delivery period starts from the date of receipt of the necessary advance as per payment terms and only when all details of contract have been made clear and both parties are in agreement with the conditions of the contact. Its strict observance presumes the fulfillment of the contractual obligations of the buyer particularly the conditions of payment agreed upon. Delivery promises are based on the current manufacturing program. We will endeavor to keep the date given, but accept no liability for failure to do so. Delay in the delivery quoted shall not render the contract as void on the part of the buyer and no claim either direct or indirect can be made on delays. In no case shall the buyer have the rights to withhold balance payment or reject goods on account of delay in delivery. We shall have the option of delivering the goods contracted in part consignments and also earlier than quoted delivery period.

The delivery period for boiler is based on adequate visits being paid to our works by the local boiler inspectorate office for inspections as per IBR and adequate power being made available.

- Terms of Payment: As per mention Above.

- Advances:

Advances paid against an order shall not be subject to any interest. We shall have the right to adjust the demurrage against such advances because of delay in lifting the ordered equipment or because of any incidental expenses we may incur on the buyer's behalf. The advance shall be forfeited in the event of cancellation of order for whatever reasons.

- Validity:

While every effort will be made to keep our quotation valid for acceptance for a period of ten days from the date hereof we may be constrained to modify this offer within this period due to circumstances beyond our control.

- Packing & Forwarding:

Packing and forwarding will be charged extra at rates prevailing at the time of supply of the equipment. Packing for dispatch will be in accordance with our standard practices.

- Insurance:

Transit insurance has to be covered by the buyer. We shall convey the dispatch particulars as soon as possible after actual dispatch to enable the buyer to arrange insurance.

- Inspection:

The boiler is made under stage-by-stage inspection during fabrication by the inspector of Steam Boilers and Smoke Nuisances, Maharashtra. It conforms to the latest Indian boiler regulations. If necessary, and called for specifically in the order the goods will be offered for vi sual inspection only at our works/our supplier's works. M/e will intimate the date of inspection about 15 days in advance. In case inspection is not carRTEd out on the date so advised, we shall be free to dispatch the consignment as per terms of delivery.

- Dispatch:

The main boiler will be dispatched in unpacked condition. All the mountings, fittings and fragile components will be dismantled and sent suitably in packed condition. Since the boiler is of package construction, the work of assembly at site is nominal and can be done easily and economically by the buyer. We shall supply the necessary assembly drawings, loading diagram and other details to facilitate the assembly work. However, if required you may avail of services of our authorized sub-contractors for erection and commissioning assistance at extra cost.

- Mode of Delivery:

All deliveRTEs will be ex our works, Pimpri / ex our supplier's works. The goods may be dispatched in one or separate lots at our option. If we are required to dispatch the goods on behalf of the purchaser we can arrange to do so by road transport only to a destination named by the purchaser, on freight to pay basis on the understanding that no liability is attached to us. The freight charges contracted by us on behalf of the buyer will be treated under the buyer's authority and shall therefore be final.

- Order Confirmation:

All orders placed on us directly or through our regional offices will be binding on us only after our head office in Pune has issued a formal order acknowledgement.

- Specifications etc.:Specifications, dimensions, designs, descriptions, shades of paints, etc. are not binding on us in minute details and are subject to reasonable alternations without notice.

- General Lien:We shall be entitled to general lien on goods in our possession or dispatched for all money due to us by the buyer, both under this contract or any other account and we shall also be entitled to apply any money in our hands under any contract due to us under any other contract or contracts.

- Warranty:

Our liability in respect of goods supplied is limited to our standard guarantee and warranty. In the case of boilers and burners, proper performance is dependent upon, amongst other factors, proper installations of chimney, connections, proper oil, water and electrical connections; use of adequate treated water and in general following of instructions specified in our service manuals with proper care and maintenance of the equipment. However, we undertake to make goods by repair (and failing which, by replacement) defects arising out of faulty design, materials or workmanship within six months of the date of dispatch. If we so require, the parts in respect of which a claim is made must be sent at buyer's expense to our works before liability can be entertained under this clause. Such expenses will be refunded if our liability is admitted. Bought outs components are guaranteed by us only to the extent of guarantees given to us by: our suppliers. Electrical components such as heaters, motors, contractors, etc. ace however not covered under this warranty. This warranty is subject to:

  - Installation having been completed within three months of dispatch of the equipment

  - The supply / installation having been formally accepted as per the handing over clause.

  - Supply of right fuel as per relevant specification available at the equipment inlet in the proper graded form and size.

  - The equipment or part thereof not being subject to accident alteration abuse or misuse

- Storage: If the goods cannot be delivered, charge will be made for stor age, insurance and interest at the rate of 1% of the Invoice value for each week or part thereof commencing 15 days from the date of Performa Invoice.

- Force Majeure:

The offer is subject to "Force Majeure" by which it means causes beyond control such as war, Invasion, civil disobedience, government orders or restrictions, lockouts, riots, fire, earthquake, floods, accidents, breakdown of machinery, delay or inability to Obtain labor, raw materials wagons, shipping, space or any other causes whatsoever beyond our reasonable control affecting us or subcontractors, suppliers etc.

- Erection and Commissioning Assistance:

After receipt of the boiler at site and if it is desired to have the services of our engineer we shall depute our engineer for the services at extra cost. To and from air and / or train fair, boarding and lodging and conveyance facilities at site will be extra at buyer's cost. These charges will be reckoned from the date of departure of our engineer from our works till the date of return to our works commissioning service offered at the rate mentioned in quotation and terms mentioned above include:

- Reasonable number of visits/meetings to help prepare the user to safely unload the material when required.

- Discussion of installation details in terms of physical/technical requirements.

- Making the user conversant with Statutory requirements if any, and discussing details of requirements in respect of power supply, feed water, fuel system etc.

- Ensuring that the installation has finally been made as recommended.

- Commissioning the unit for a short run from the point of view of mechanical working and to set necessary.

- Conducting demonstration for the purpose of user's education for equipment operation and maintenance.

- The buyer against Performa Invoice Prior to delivery shall pay the above charges.

- Handing Over:

Unless otherwise specified in the order and accepted handing over of the equipment and/or installation would be considered as completed and a formal completion certificate shall be issued by the buyer/user, if

The material has been supplied as per the terms and scope of supply with agreed deviations, if any.

- Erection if involved has been completed generally as per terms of order with unavoidable Deviations.

- The equipment has been commissioned, if applicable, generally as agreed.

- The equipment and /or installation has been put to commercial use either with or without help of our engineer.

The buyer/ user is expected to put the equipment to commercial use only after issuing a formal completion certificate. Our responsibility in terms of warranty shall cease straightaway if the equipment is put to use without formal taking over.

- Boiler Registration:RELIABLE THERMAL ENGINEERS boiler is made as per Indian Boiler Regulations / BS-2790 and hence a set of relevant documents and certificates signed by the Chief Inspector Of Boilers, Maharashtra or any other agreed approval agency is provided for each boiler. All preparations for hydraulic test, open inspection and other IBR formalities to be completed for registration by the boiler inspectors of the concerned state would be made by the buyer at his cost.

- Secrecy Of Documents / Information

We undertake to provide such drawings, design calculations and fabrication details in support of the boiler supplied together with material as well as test and hydraulic certificates which are mandatory and required for the purpose of acceptance and registration of the boiler by the receiving party.

- Cancellation: All orders received and acknowledged by us shall not be subject to cancellation either wholly or partly far any reason whatsoever. in the event of cancellation of an order, the advance shall be forfeited.

- Jurisdiction:

All contracts between the buyer and ourselves are deemed to be entered into at Pune and are therefore, subject to the jurisdiction of courts at Pune.

- General: Any condition or other matters relating to this quotation not expressly stipulated will be a matter of mutual discussion and agreement at the time of accepting the order. If this quotation is accepted and an order is placed, all the above conditions of sale stand automatically accepted.

In order to offer our clients the advantage of the latest technical development and progress, we reserve the right to amend details of design without notice.