Ref: GAS/R/0820/010A					Date: 10 August  2020

To

Mr. Subhash Patil,

Shree Mahaganapati Agro Producer Co.Ltd.

Thanapude, Tal- Walva, Sangali,  Maharashtra, India

SUBJECT: PROPOSAL FOR PRECOOLING 3MT & COLD ROOM 10 MT .

Dear Sir,

We take this opportunity to inform you that, we have successfully implemented several projects for Cold Rooms.

We are pleased to submit our final and competitive detailed offer comprising of;

- Product Summery & Commercial terms and conditions

- Technical Specifications

- Scope of supply

We hope the above details are in line with your requirement and we now look forward to receive your valued order at the earliest.

Should you require further clarifications / Information, Please feel free to contact us.

Assuring our Best of services always.

Thanking You,

Yours truly,

Mr. Zunzar Patil

Green Agritech Services.

- Supply of PUF sandwich panel’s floor puf Slabs, Hinged doors, Puf density 40 Kg/m3 PPGI 0.5mm for Wall and Ceiling Panel with Prefab Puf.  Including Installation accessories like angle flasher, rivets and Sealants etc. For Floor Insulation Loose Puf slabs, Vapor Barrier Polythene Sheets etc. will be supplied by us for laying prior to Flooring work (Kota stone) which to be carried out by customer at own expenses. (Customer’s Scope)

- COLD ROOM SIZE (External Dimension)

|  | Length | Width | Height | Qty. |
| --- | --- | --- | --- | --- |
| Pre Cooling 3MT 3Hrs Batch 80 mm | 4.0 M 13.1 Ft | 3.0 M 9.8 Ft | 3.0 M 9.8 Ft | 1 No. |
| Cold Room 10 MT 60 mm | 5.0 M 16.4 Ft | 4.5 M 14.8 Ft | 3.0 M 9.8 Ft | 1 No. |

Wall & Ceiling Panel Area 		143 Square Meter.

Floor Panel Area			 34  Square Meter.

PUF Panel thickness			 80/ 60 mm

Product :- Babycorn

- Hinge Door

| Width | Height | Thickness | Qty. |
| --- | --- | --- | --- |
| 900 mm | 2100 mm | 60 mm | 2 Nos. |

- Puf  Panel  and Doors 							Rs.5,42,665/-

- Condensing Unit & Evaporating Unit (3 TR 2 Nos. & 5TR 01)	Rs.8,80,000/-

Air cooled condensing of with suitable hermetically sealed

Compressor to achieve the above temperature with

EMERSON/TECUMSEH Make comp. complete

With receiver, Service valves, Driers, Liquid Solenoid valves.

Temperature Control Panel

Under/Over Voltage Protection Single Phase and Phase reversal safety

Minilec /Subzero Make High Pressure & Low Pressure Protection Inbuilt

In condensing unit. Cold Room Controller Fitted in Control Panel Box

With MCB, Indicating Lamps, Contactors, Overload Relay Etc.

Total Material Supply Cost    				   		Rs.14,22,665/-

GST@18% Inclusive

Installation & Commissioning charges Inclusive

Transportation Cost Extra your Scope.

TECHNICAL PARAMETRS

| MODEL | ARB-30 &50 Pre cooling 1 No & Cold Room 2 Nos |
| --- | --- |
| Room Dimensions to be maintained | About area of each Rooms 127 & 242 Sq. Feet With Max Height of 9.8 feet |
| Design Room Temperature | 0°C ( Product Babycorn) |
| Indoor cooling unit | Fan Motors 300 mm Dia. x 2 Nos. 2E-300 High speed Air flow 5000 Cu.Mtr/Hr Type Ceiling Suspended with Air Defrost |
| COMPRESSOR DATA |  |
| Type | Hermetic compressor Emerson make 3.0TR & 5 TR |
| Refrigerant ( First Charge ) | R-404a |
| Brake Horse Power (BHP) (Approx) and Cooling Capacity | 4.0 36000 & 60000 BTU/Hr at -7 Deg Evap. for pre cooling + 45 Deg Condensing Temp. |
| CONDENSER DATA |  |
| Mode Of Cooling | AIR COOLED Horizontal Discharge Of Air With Service Valve and Filter Dryer, Receiver, Solenoid valve, HP LP switches |
| Type | TUBE AND FINNED COIL |
| CONTROL PANEL | Single Phasing, Under/Over Voltage Protection |
| Single Phase and phase reversal safety | Selec Make |
| High Pressure & Low Pressure Protection | Inbuilt in condensing unit |
| Cold Room Controller | Fitted in Control Panel Box with MCB, Indicating Lamps, Contactors, Overload Relay Etc. |

#### TERMS & CONDITIONS

Validity: -

Our offer is open for acceptance for a period of 30 days from the date of this offer and thereafter it shall be subject to our written confirmation.

Specifications: -

In line with our policy of continual improvement we reserve the right to modify the design and change the specifications of any material, if in our opinion such Modification constitutes an improvement or is in accordance with revised standards of manufacturing methods. Therefore, specifications, illustrations, dimensions and weights given or agreed to by us in our proposal, catalogues, drawings, Photographs etc. are not binding in detail and are approximate only.

Price: -

The quoted prices are on Ex Pune basis, Transport charges Extra

GST: -

GST Inclusive in Above Prices.

Insurance: -

All equipment and materials to be supplied against customer’s risk. If customer desire to opt for transit insurance, it is to be intimated in advance and extra charges to be borne by customer.

Delivery Period: -

3-4 weeks from the receipt of your technically and commercially clear order with advance. The delivery period is indicated in good faith. We will Endeavour to keep the delivery schedule, which is based on current manufacturing program. The above delivery is subject to force Majeure. Delay in delivery will not render the contract void able or reject goods on Account of delay in delivery.

Terms of Payment: -

70% advance along with the purchase order and balance 25% should be released against Delivery note before dispatch & remaining 5% immediately after completion of installation work

Warranty: -

Subject to terms of payment agreed upon being punctually complied With and the equipment being operated properly, the machinery covered by this Contract carries a Warranty against manufacturing defects for 12 months from the date of installation, If any Part of the equipment is put to use earlier for any reason, whatsoever, the warranty Period will commence from the date of such use.

We agree to repair / replace such parts which may prove defective and which do not fail from neglect or misuse or faulty operation. Should, However, the services of our qualified men be required outside limits Our Standard charges for such services will apply

Property Rights and General Lien: -

As unpaid vendors we shall retain the property rights in the equipment and material Supplied by us under this contract and our rights of lien and resale, until full value thereof as per our bill is paid to us.

During installation & commissioning certain materials deliberately sent in extra quantity to avoid inconvenience. Any such extra material after finishing installation job remains the property of Company and will be taken back suitably. Customer should not claim for such excess material.

Limitation to Liability: -

In no event shall we be liable for any consequential loss or damage arising out of or connected with this order in any way whatsoever.

Cancellation Charges: -

If any order or part of the order is cancelled, the same shall be subject to cancellation charges including compensation for costs, expenses and losses incurred by us up to the date of cancellation.

Force Majeure: -

No liability shall attach to us for non-performance or delayed execution of this order as a result of force majeure.

Liquidated Damages:-

Notwithstanding anything to the contrary, we regret our inability to be liable for any Liquidated damages on account of delay of supply / installation for any reason whatsoever.

Inspection:-

Inspection of goods shall be arranged at our premises

SCOPE OF WORK

Our scope of work includes installation, testing and commissioning of your Initial Setting up of Cold Storage for your room(s).

CUSTOMER SCOPE

(Customer has to carry out following work at his own expenses)

- Stable Voltage 380-430 Volts Electrical Supply with suitable Breaker (MCB) and Power Distribution Panel near to units and lighting work within and outside rooms.

- All sort of Civil & fabrication Work, Kota Flooring, Water Line Plumbing etc. work as required.

- Water, light, electricity and covered storage space shall be provided to us free of Cost near the work site.

- Support for various equipments will be provided by the customer.

- Unloading of all the equipments at site and safe storage of the same shall be buyer’s responsibility.

- Staying and food arrangement for 3 to 4 person during installation.